## Summary SBMS Registers
Modbus TCP: Summary Registers
Updated 28 Sept 2021
Register Set for Each Battery Pack | [6 empty] | Register Locations for Each Battery Pack |  |  |  |  | Alarms: Battery Pack (Battery Pack Register Offset 7)
Register Offset | Example Register (Battery Pack 1) |  | Friendly Name | Units | Data Type | Description | Batery Pack | First Register |  | Last Register Location |  | Bit Index | Friendly Name | Description
| Type | Location | [5 empty] | Type | Location | Type | Location
0 | 4 | 01001 | Battery Pack Serial Number (MSW) | n/a | uint16 | The most significant 16-bits of a 32-bit battery pack serial number. | Battery pack #20 | 4 | 1381 | 4 | 1400 | 0 | Over Voltage | 1 = Battery pack over voltage condition, 0 = No such condition.
1 | 4 | 01002 | Battery Pack Serial Number (LSW) | n/a | uint16 | The least significant 16-bits of a 32-bit battery pack serial number. | Battery pack #19 | 4 | 1361 | 4 | 1380 | 1 | Under Voltage | 1 = Battery pack under voltage condition, 0 = No such condition.
2 | 4 | 01003 | Battery Pack Voltage (MSW) | mV | uint16 | The most significant 16-bits of a 32-bit battery pack voltage. | Battery pack #18 | 4 | 1341 | 4 | 1360 | 2 | Over Current | 1 = Battery pack over currrent condition, 0 = No such condition.
3 | 4 | 01004 | Battery Pack Voltage (LSW) | mV | uint16 | The least significant 16-bits of a 32-bit battery pack voltage. | Battery pack #17 | 4 | 1321 | 4 | 1340 | 3 | Over Temperature | 1 = Battery pack over temperature condition, 0 = No such condition.
4 | 4 | 01005 | Battery Pack Average Current (MSW) | mA | int16 | The most significant 16-bits of a 32-bit current into (out of) the battery pack, averaged over the last 30 secs. | Battery pack #16 | 4 | 1301 | 4 | 1320 | 4 | Reserved | Guaranteed to be 0 when no alarms active.
5 | 4 | 01006 | Battery Pack Average Current (LSW) | mA | int16 | The least significant 16-bits of a 32-bit current into (out of) the battery pack, averaged over the last 30 secs. | Battery pack #15 | 4 | 1281 | 4 | 1300 | 5 | Reserved | Guaranteed to be 0 when no alarms active.
6 | 4 | 01007 | Battery Pack Average Temperature | °C | int16 | The temperature inside the battery pack averaged over the last 30 secs. | Battery pack #14 | 4 | 1261 | 4 | 1280 | 6 | Reserved | Guaranteed to be 0 when no alarms active.
7 | 4 | 01008 | Alarms: Battery Pack | n/a | bitfield16 | Zero when no battery pack alarms active. See the separate table for more details. | Battery pack #13 | 4 | 1241 | 4 | 1260 | 7 | Reserved | Guaranteed to be 0 when no alarms active.
8 | 4 | 01009 | Alarms: System (Future Provision) | n/a | bitfield16 | Zero when no system alarms active. See the separate table for more details. | Battery pack #12 | 4 | 1221 | 4 | 1240 | 8 | Reserved | Guaranteed to be 0 when no alarms active.
9 | 4 | 01010 | Battery Pack State of Charge (Not in Use) | % | uint16 | [Not in use] The state of charge of the battery pack (integers from 0 to 100). | Battery pack #11 | 4 | 1201 | 4 | 1220 | 9 | Reserved | Guaranteed to be 0 when no alarms active.
10 | 4 | 01011 | System Sign of Life | n/a | uint16 | A value which changes each time the register set is updated. | Battery pack #10 | 4 | 1181 | 4 | 1200 | 10 | Reserved | Guaranteed to be 0 when no alarms active.
11 | 4 | 01012 | Reserved | n/a | n/a | n/a | Battery pack #09 | 4 | 1161 | 4 | 1180 | 11 | Reserved | Guaranteed to be 0 when no alarms active.
12 | 4 | 01013 | Reserved | n/a | n/a | n/a | Battery pack #08 | 4 | 1141 | 4 | 1160 | 12 | Reserved | Guaranteed to be 0 when no alarms active.
13 | 4 | 01014 | Reserved | n/a | n/a | n/a | Battery pack #07 | 4 | 1121 | 4 | 1140 | 13 | Reserved | Guaranteed to be 0 when no alarms active.
14 | 4 | 01015 | Reserved | n/a | n/a | n/a | Battery pack #06 | 4 | 1101 | 4 | 1120 | 14 | Reserved | Guaranteed to be 0 when no alarms active.
15 | 4 | 01016 | Reserved | n/a | n/a | n/a | Battery pack #05 | 4 | 1081 | 4 | 1100 | 15 | Reserved | Guaranteed to be 0 when no alarms active.
16 | 4 | 01017 | Reserved | n/a | n/a | n/a | Battery pack #04 | 4 | 1061 | 4 | 1080
17 | 4 | 01018 | Reserved | n/a | n/a | n/a | Battery pack #03 | 4 | 1041 | 4 | 1060 | [FUTURE PROVISION] Alarms: System (Battery Pack Register Offset 8)
18 | 4 | 01019 | Reserved | n/a | n/a | n/a | Battery pack #02 | 4 | 1021 | 4 | 1040 | Bit Index | Friendly Name | Description
19 | 4 | 01020 | Reserved | n/a | n/a | n/a | Battery pack #01 | 4 | 1001 | 4 | 1020
[12 empty] | 0 | Reserved | Guaranteed to be 0 when no alarms active.
[12 empty] | 1 | Reserved | Guaranteed to be 0 when no alarms active.
Notes: | [11 empty] | 2 | Reserved | Guaranteed to be 0 when no alarms active.
1. Each battery pack in the rack has 20 registers allocated, although some of the registers are reserved. | [11 empty] | 3 | Reserved | Guaranteed to be 0 when no alarms active.
2. Battery pack #01 (1st battery) is defined as the bottom battery in the rack. | [11 empty] | 4 | Reserved | Guaranteed to be 0 when no alarms active.
3. Battery pack #20 (20th battery) is defined as the top battery in a rack of 20 batteries. | [11 empty] | 5 | Reserved | Guaranteed to be 0 when no alarms active.
4. Battery pack #01 occupies register locations [4]01001 to [4]01020. | [11 empty] | 6 | Reserved | Guaranteed to be 0 when no alarms active.
5. Battery pack #02 occupies register locations [4]01021 to [4]01040. | [11 empty] | 7 | Reserved | Guaranteed to be 0 when no alarms active.
6. Battery pack #N occupies register locations ([4]01001 + (N-1)*20) to ([4]01020 + (N-1)*20). | [11 empty] | 8 | Reserved | Guaranteed to be 0 when no alarms active.
7. All registers are 'holding registers' (register type 4). | [11 empty] | 9 | Reserved | Guaranteed to be 0 when no alarms active.
8. At the physical protocol layer, the register address in the PDU packet is the register location given in this document with the type [4] dropped and with 1 subtracted. Eg. Register location [4]01001 = physical address 1,000. | [11 empty] | 10 | Reserved | Guaranteed to be 0 when no alarms active.
[12 empty] | 11 | Reserved | Guaranteed to be 0 when no alarms active.
[12 empty] | 12 | Reserved | Guaranteed to be 0 when no alarms active.
[12 empty] | 13 | Reserved | Guaranteed to be 0 when no alarms active.
[12 empty] | 14 | Reserved | Guaranteed to be 0 when no alarms active.
[12 empty] | 15 | Reserved | Guaranteed to be 0 when no alarms active.

## Detailed SBMS Registers
Modbus TCP: Registers
Updated 28 Sept 2021
Register Set for Each Battery Pack | [6 empty] | Register Locations for Each Battery Pack
Register Offset | Example Register (Battery Pack 1) |  | Friendly Name | Units | Data Type | Description | Batery Pack | First Register |  | Last Register Location
| Type | Location | [5 empty] | Type | Location | Type | Location
0 | 4 | 10001 | Battery Pack Serial Number (MSW) | n/a | uint16 | The most significant 16-bits of a 32-bit battery pack serial number. | Battery pack #20 | 4 | 11901 | 4 | 12000
1 | 4 | 10002 | Battery Pack Serial Number (LSW) | n/a | uint16 | The least significant 16-bits of a 32-bit battery pack serial number. | Battery pack #19 | 4 | 11801 | 4 | 11900
2 | 4 | 10003 | Cell String 01 Voltage | mV | uint16 | The voltage across the parallel cells of string 1. | Battery pack #18 | 4 | 11701 | 4 | 11800
3 | 4 | 10004 | Cell String 02 Voltage | mV | uint16 | The voltage across the parallel cells of string 2. | Battery pack #17 | 4 | 11601 | 4 | 11700
4 | 4 | 10005 | Cell String 03 Voltage | mV | uint16 | The voltage across the parallel cells of string 3. | Battery pack #16 | 4 | 11501 | 4 | 11600
5 | 4 | 10006 | Cell String 04 Voltage | mV | uint16 | The voltage across the parallel cells of string 4. | Battery pack #15 | 4 | 11401 | 4 | 11500
6 | 4 | 10007 | Cell String 05 Voltage | mV | uint16 | The voltage across the parallel cells of string 5. | Battery pack #14 | 4 | 11301 | 4 | 11400
7 | 4 | 10008 | Cell String 06 Voltage | mV | uint16 | The voltage across the parallel cells of string 6. | Battery pack #13 | 4 | 11201 | 4 | 11300
8 | 4 | 10009 | Cell String 07 Voltage | mV | uint16 | The voltage across the parallel cells of string 7. | Battery pack #12 | 4 | 11101 | 4 | 11200
9 | 4 | 10010 | Cell String 08 Voltage | mV | uint16 | The voltage across the parallel cells of string 8. | Battery pack #11 | 4 | 11001 | 4 | 11100
10 | 4 | 10011 | Cell String 09 Voltage | mV | uint16 | The voltage across the parallel cells of string 9. | Battery pack #10 | 4 | 10901 | 4 | 11000
11 | 4 | 10012 | Cell String 10 Voltage | mV | uint16 | The voltage across the parallel cells of string 10. | Battery pack #09 | 4 | 10801 | 4 | 10900
12 | 4 | 10013 | Cell String 11 Voltage | mV | uint16 | The voltage across the parallel cells of string 11. | Battery pack #08 | 4 | 10701 | 4 | 10800
13 | 4 | 10014 | Cell String 12 Voltage | mV | uint16 | The voltage across the parallel cells of string 12. | Battery pack #07 | 4 | 10601 | 4 | 10700
14 | 4 | 10015 | Cell String 13 Voltage | mV | uint16 | The voltage across the parallel cells of string 13. | Battery pack #06 | 4 | 10501 | 4 | 10600
15 | 4 | 10016 | Cell String 14 Voltage | mV | uint16 | The voltage across the parallel cells of string 14. | Battery pack #05 | 4 | 10401 | 4 | 10500
16 | 4 | 10017 | Cell String 15 Voltage | mV | uint16 | The voltage across the parallel cells of string 15. | Battery pack #04 | 4 | 10301 | 4 | 10400
17 | 4 | 10018 | Cell String 16 Voltage | mV | uint16 | The voltage across the parallel cells of string 16. | Battery pack #03 | 4 | 10201 | 4 | 10300
18 | 4 | 10019 | Cell String 17 Voltage | mV | uint16 | The voltage across the parallel cells of string 17. | Battery pack #02 | 4 | 10101 | 4 | 10200
19 | 4 | 10020 | Cell String 18 Voltage | mV | uint16 | The voltage across the parallel cells of string 18. | Battery pack #01 | 4 | 10001 | 4 | 10100
20 | 4 | 10021 | Cell String 19 Voltage | mV | uint16 | The voltage across the parallel cells of string 19.
21 | 4 | 10022 | Cell String 20 Voltage | mV | uint16 | The voltage across the parallel cells of string 20.
22 | 4 | 10023 | Cell String 21 Voltage | mV | uint16 | The voltage across the parallel cells of string 21.
23 | 4 | 10024 | Cell String 22 Voltage | mV | uint16 | The voltage across the parallel cells of string 22.
24 | 4 | 10025 | Cell String 23 Voltage | mV | uint16 | The voltage across the parallel cells of string 23.
25 | 4 | 10026 | Cell String 24 Voltage | mV | uint16 | The voltage across the parallel cells of string 24.
26 | 4 | 10027 | Cell String 25 Voltage | mV | uint16 | The voltage across the parallel cells of string 25.
27 | 4 | 10028 | Cell String 26 Voltage | mV | uint16 | The voltage across the parallel cells of string 26.
28 | 4 | 10029 | Cell String 27 Voltage | mV | uint16 | The voltage across the parallel cells of string 27.
29 | 4 | 10030 | Cell String 28 Voltage | mV | uint16 | The voltage across the parallel cells of string 28.
30 | 4 | 10031 | Cell String 29 Voltage | mV | uint16 | The voltage across the parallel cells of string 29.
31 | 4 | 10032 | Cell String 30 Voltage | mV | uint16 | The voltage across the parallel cells of string 30.
32 | 4 | 10033 | Cell String 31 Voltage | mV | uint16 | The voltage across the parallel cells of string 31.
33 | 4 | 10034 | Cell String 32 Voltage | mV | uint16 | The voltage across the parallel cells of string 32.
34 | 4 | 10035 | Cell String 33 Voltage | mV | uint16 | The voltage across the parallel cells of string 33.
35 | 4 | 10036 | Cell String 34 Voltage | mV | uint16 | The voltage across the parallel cells of string 34.
36 | 4 | 10037 | Cell String 35 Voltage | mV | uint16 | The voltage across the parallel cells of string 35.
37 | 4 | 10038 | Cell String 36 Voltage | mV | uint16 | The voltage across the parallel cells of string 36.
38 | 4 | 10039 | Cell String 37 Voltage | mV | uint16 | The voltage across the parallel cells of string 37.
39 | 4 | 10040 | Cell String 38 Voltage | mV | uint16 | The voltage across the parallel cells of string 38.
40 | 4 | 10041 | Cell String 39 Voltage | mV | uint16 | The voltage across the parallel cells of string 39.
41 | 4 | 10042 | Cell String 40 Voltage | mV | uint16 | The voltage across the parallel cells of string 40.
42 | 4 | 10043 | Battery Pack Voltage (MSW) | mV | uint16 | The most significant 16-bits of a 32-bit battery pack voltage.
43 | 4 | 10044 | Battery Pack Voltage (LSW) | mV | uint16 | The least significant 16-bits of a 32-bit battery pack voltage.
44 | 4 | 10045 | Battery Pack Average Current (MSW) | mA | int16 | The most significant 16-bits of a 32-bit current into (out of) the battery pack, averaged over the last 30 secs.
45 | 4 | 10046 | Battery Pack Average Current (LSW) | mA | int16 | The least significant 16-bits of a 32-bit current into (out of) the battery pack, averaged over the last 30 secs.
46 | 4 | 10047 | Battery Pack Average Temperature | °C | int16 | The temperature inside the battery pack averaged over the last 30 secs.
47 | 4 | 10048 | Alarms: Battery Pack | n/a | bitfield16 | Zero when no battery pack alarms active. See the separate table (on the Summary Registers' sheet) for more details.
48 | 4 | 10049 | Alarms: System (Future Provision) | n/a | bitfield16 | Zero when no system alarms active. See the separate table (on the Summary Registers' sheet) for more details.
49 | 4 | 10050 | Reserved | n/a | n/a | n/a
50 | 4 | 10051 | System Sign of Life | n/a | uint16 | A value which changes each time the register set is updated.
51 | 4 | 10052 | Reserved | n/a | n/a | n/a
52 | 4 | 10053 | Reserved | n/a | n/a | n/a
53 | 4 | 10054 | Reserved | n/a | n/a | n/a
54 | 4 | 10055 | Reserved | n/a | n/a | n/a
55 | 4 | 10056 | Reserved | n/a | n/a | n/a
56 | 4 | 10057 | Reserved | n/a | n/a | n/a
57 | 4 | 10058 | Reserved | n/a | n/a | n/a
58 | 4 | 10059 | Reserved | n/a | n/a | n/a
59 | 4 | 10060 | Reserved | n/a | n/a | n/a
60 | 4 | 10061 | Reserved | n/a | n/a | n/a
61 | 4 | 10062 | Reserved | n/a | n/a | n/a
62 | 4 | 10063 | Reserved | n/a | n/a | n/a
63 | 4 | 10064 | Reserved | n/a | n/a | n/a
64 | 4 | 10065 | Reserved | n/a | n/a | n/a
65 | 4 | 10066 | Reserved | n/a | n/a | n/a
66 | 4 | 10067 | Reserved | n/a | n/a | n/a
67 | 4 | 10068 | Reserved | n/a | n/a | n/a
68 | 4 | 10069 | Reserved | n/a | n/a | n/a
69 | 4 | 10070 | Reserved | n/a | n/a | n/a
70 | 4 | 10071 | Reserved | n/a | n/a | n/a
71 | 4 | 10072 | Reserved | n/a | n/a | n/a
72 | 4 | 10073 | Reserved | n/a | n/a | n/a
73 | 4 | 10074 | Reserved | n/a | n/a | n/a
74 | 4 | 10075 | Reserved | n/a | n/a | n/a
75 | 4 | 10076 | Reserved | n/a | n/a | n/a
76 | 4 | 10077 | Reserved | n/a | n/a | n/a
77 | 4 | 10078 | Reserved | n/a | n/a | n/a
78 | 4 | 10079 | Reserved | n/a | n/a | n/a
79 | 4 | 10080 | Reserved | n/a | n/a | n/a
80 | 4 | 10081 | Reserved | n/a | n/a | n/a
81 | 4 | 10082 | Reserved | n/a | n/a | n/a
82 | 4 | 10083 | Reserved | n/a | n/a | n/a
83 | 4 | 10084 | Reserved | n/a | n/a | n/a
84 | 4 | 10085 | Reserved | n/a | n/a | n/a
85 | 4 | 10086 | Reserved | n/a | n/a | n/a
86 | 4 | 10087 | Reserved | n/a | n/a | n/a
87 | 4 | 10088 | Reserved | n/a | n/a | n/a
88 | 4 | 10089 | Reserved | n/a | n/a | n/a
89 | 4 | 10090 | Reserved | n/a | n/a | n/a
90 | 4 | 10091 | Reserved | n/a | n/a | n/a
91 | 4 | 10092 | Reserved | n/a | n/a | n/a
92 | 4 | 10093 | Reserved | n/a | n/a | n/a
93 | 4 | 10094 | Reserved | n/a | n/a | n/a
94 | 4 | 10095 | Reserved | n/a | n/a | n/a
95 | 4 | 10096 | Reserved | n/a | n/a | n/a
96 | 4 | 10097 | Reserved | n/a | n/a | n/a
97 | 4 | 10098 | Reserved | n/a | n/a | n/a
98 | 4 | 10099 | Reserved | n/a | n/a | n/a
99 | 4 | 10100 | Reserved | n/a | n/a | n/a
Notes:
1. Each battery pack in the rack has 100 registers allocated, although some of the registers are reserved.
2. Battery pack #01 (1st battery) is defined as the bottom battery in the rack.
3. Battery pack #20 (20th battery) is defined as the top battery in a rack of 20 batteries.
4. Battery pack #01 occupies register locations [4]10001 to [4]10100.
5. Battery pack #02 occupies register locations [4]10101 to [4]10200.
6. Battery pack #N occupies register locations ([4]10001 + (N-1)*100) to ([4]10100 + (N-1)*100).
7. All registers are 'holding registers' (register type 4).
8. At the physical protocol layer, the register address in the PDU packet is the register location given in this document with the type [4] dropped and with 1 subtracted. Eg. Register location [4]10001 = physical address 10,000.

## System Summary Registers
Modbus TCP: SwitchDin Registers (Device Summary Information)
Updated 28 Sept 2021
Type | Location | Friendly Name | Units | Data Type | Description
4 | 00201 | Manufacturer Name (MSW) | n/a | uint16 | The most significant 16-bits of a 32-bit
4 | 00202 | Manufacturer Name (LSW) | n/a | uint16 | The least significant 16-bits of a 32-bit
4 | 00203 | Model Number Major Value | n/a | uint16
4 | 00204 | Model Number Minor Value | n/a | uint16
4 | 00205 | Firmware Version Major Value | n/a | uint16
4 | 00206 | Firmware Version Minor Value | n/a | uint16
4 | 00207 | MSM Serial Number (MSW) | n/a | uint16 | The most significant 16-bits of a 32-bit number
4 | 00208 | MSM Serial Number (LSW) | n/a | uint16 | The least significant 16-bits of a 32-bit number
4 | 00209 | Reserved | n/a | n/a | n/a
4 | 00210 | Reserved | n/a | n/a | n/a
4 | 00211 | Reserved | n/a | n/a | n/a
4 | 00212 | Reserved | n/a | n/a | n/a
4 | 00213 | Reserved | n/a | n/a | n/a
4 | 00214 | Reserved | n/a | n/a | n/a
4 | 00215 | Reserved | n/a | n/a | n/a
4 | 00216 | Reserved | n/a | n/a | n/a
4 | 00217 | Reserved | n/a | n/a | n/a
4 | 00218 | Reserved | n/a | n/a | n/a
4 | 00219 | Reserved | n/a | n/a | n/a
4 | 00220 | Reserved | n/a | n/a | n/a
4 | 00221 | Reserved | n/a | n/a | n/a
4 | 00222 | Reserved | n/a | n/a | n/a
4 | 00223 | Reserved | n/a | n/a | n/a
4 | 00224 | Reserved | n/a | n/a | n/a
4 | 00225 | Reserved | n/a | n/a | n/a
4 | 00226 | Reserved | n/a | n/a | n/a
4 | 00227 | Reserved | n/a | n/a | n/a
4 | 00228 | Reserved | n/a | n/a | n/a
4 | 00229 | Reserved | n/a | n/a | n/a
4 | 00230 | Reserved | n/a | n/a | n/a
4 | 00231 | Reserved | n/a | n/a | n/a
4 | 00232 | Reserved | n/a | n/a | n/a
4 | 00233 | Reserved | n/a | n/a | n/a
4 | 00234 | Reserved | n/a | n/a | n/a
4 | 00235 | Reserved | n/a | n/a | n/a
4 | 00236 | Reserved | n/a | n/a | n/a
4 | 00237 | Reserved | n/a | n/a | n/a
4 | 00238 | Reserved | n/a | n/a | n/a
4 | 00239 | Reserved | n/a | n/a | n/a
4 | 00240 | Reserved | n/a | n/a | n/a
4 | 00241 | Reserved | n/a | n/a | n/a
4 | 00242 | Reserved | n/a | n/a | n/a
4 | 00243 | Reserved | n/a | n/a | n/a
4 | 00244 | Reserved | n/a | n/a | n/a
4 | 00245 | Reserved | n/a | n/a | n/a
4 | 00246 | Reserved | n/a | n/a | n/a
4 | 00247 | Reserved | n/a | n/a | n/a
4 | 00248 | Reserved | n/a | n/a | n/a
4 | 00249 | Reserved | n/a | n/a | n/a
4 | 00250 | Reserved | n/a | n/a | n/a
4 | 00251 | Reserved | n/a | n/a | n/a

## SwitchDin Rack Registers
Modbus TCP: SwitchDin Registers (Device Rack Information)
Updated 18 Oct 2021
Offset | Example Register (Rack 01) |  | Friendly Name | Units | Data Type | Description | Device Availability
| Type | Location |  |  |  |  | Venus | Lynx | BMV
0 | 4 | 00301 | Reserved | n/a | n/a | n/a
1 | 4 | 00302 | Reserved | n/a | n/a | n/a
2 | 4 | 00303 | Reserved | n/a | n/a | n/a
3 | 4 | 00304 | Reserved | n/a | n/a | n/a
4 | 4 | 00305 | Reserved | n/a | n/a | n/a
5 | 4 | 00306 | Reserved | n/a | n/a | n/a
6 | 4 | 00307 | Rack SBMS Connected Count | n/a | uint16 |  | y | y | y
7 | 4 | 00308 | Rack Total Power Charged (MSW) | 1/10 kWh | uint16 | The most significant 16-bits of a 32-bit number | y | n | y
8 | 4 | 00309 | Rack Total Power Charged (LSW) | 1/10 kWh | uint16 | The least significant 16-bits of a 32-bit number | y | n | y
9 | 4 | 00310 | Rack Total Power Discharged (MSW) | 1/10 kWh | uint16 | The most significant 16-bits of a 32-bit number | y | n | y
10 | 4 | 00311 | Rack Total Power Discharged (LSW) | 1/10 kWh | uint16 | The least significant 16-bits of a 32-bit number | y | n | y
11 | 4 | 00312 | State of Charge | % | uint16 |  | y | y | y
12 | 4 | 00313 | Rack Temperature | 1 C | int16 | *Available with external temeperature sensor attached. | y | y | y
13 | 4 | 00314 | Rack Voltage (MSW) | mV | uint16 | The most significant 16-bits of a 32-bit number | y | y | y
14 | 4 | 00315 | Rack Voltage (LSW) | mV | uint16 | The least significant 16-bits of a 32-bit number | y | y | y
15 | 4 | 00316 | Rack Current (MSW) | mA | int16 | The most significant 16-bits of a 32-bit number | y | y | y
16 | 4 | 00317 | Rack Current (LSW) | mA | int16 | The least significant 16-bits of a 32-bit number | y | y | y
17 | 4 | 00318 | Rack Power (MSW) | W | int16 | The most significant 16-bits of a 32-bit number | y | y | y
18 | 4 | 00319 | Rack Power (LSW) | W | int16 | The least significant 16-bits of a 32-bit number | y | y | y
19 | 4 | 00320 | State of Charge Sync Status | n/a | uint16 | 1-State of Charge is Synchronized on External Device, 0-It is not | n | n | y
20 | 4 | 00321 | State of Charge Sync Count | n/a | uint16 | Count of times the State of Charge is Synchronized on External Device | y | y | y
21 | 4 | 00322 | System Capacity | Ah | uint16 | Rack Total Battery Capacity (Based on Installation) | y | n | y
22 | 4 | 00323 | Reserved | n/a | n/a | n/a
23 | 4 | 00324 | Reserved | n/a | n/a | n/a
24 | 4 | 00325 | Reserved | n/a | n/a | n/a
25 | 4 | 00326 | Reserved | n/a | n/a | n/a
26 | 4 | 00327 | Reserved | n/a | n/a | n/a
27 | 4 | 00328 | Reserved | n/a | n/a | n/a
28 | 4 | 00329 | Reserved | n/a | n/a | n/a
29 | 4 | 00330 | Reserved | n/a | n/a | n/a
30 | 4 | 00331 | Reserved | n/a | n/a | n/a
31 | 4 | 00332 | Reserved | n/a | n/a | n/a
32 | 4 | 00333 | Reserved | n/a | n/a | n/a
33 | 4 | 00334 | Reserved | n/a | n/a | n/a
34 | 4 | 00335 | Reserved | n/a | n/a | n/a
35 | 4 | 00336 | Reserved | n/a | n/a | n/a
36 | 4 | 00337 | Reserved | n/a | n/a | n/a
37 | 4 | 00338 | Reserved | n/a | n/a | n/a
38 | 4 | 00339 | Reserved | n/a | n/a | n/a
39 | 4 | 00340 | Reserved | n/a | n/a | n/a
40 | 4 | 00341 | Reserved | n/a | n/a | n/a
41 | 4 | 00342 | Reserved | n/a | n/a | n/a
42 | 4 | 00343 | Reserved | n/a | n/a | n/a
43 | 4 | 00344 | Reserved | n/a | n/a | n/a
44 | 4 | 00345 | Reserved | n/a | n/a | n/a
45 | 4 | 00346 | Reserved | n/a | n/a | n/a
46 | 4 | 00347 | Reserved | n/a | n/a | n/a
47 | 4 | 00348 | Reserved | n/a | n/a | n/a
48 | 4 | 00349 | Reserved | n/a | n/a | n/a
49 | 4 | 00350 | Reserved | n/a | n/a | n/a
50 | 4 | 00351 | Reserved | n/a | n/a | n/a

## MSM Summary
Modbus TCP: Summary Blocks of Registers
Updated July 7, 2021
Register Block | Start |  | End |  | Notes
| Type | Address | Type | Address
Inverter Register Block | 4 | 1 | 4 | 103 | Only used for specific customer that implemented Inverter Schedule
SwitchDin MSM Info Register Block | 4 | 201 | 4 | 250 | For SwitchDin Droplet (but generic enough)
SwitchDin Rack Info #01 | 4 | 301 | 4 | 350 | Only Rack 01 is implemented
SwitchDin Rack Info #02 | 4 | 401 | 4 | 450
SwitchDin Rack Info #03 | 4 | 501 | 4 | 550
SwitchDin Rack Info #04 | 4 | 601 | 4 | 650
SwitchDin Rack Info #05 | 4 | 701 | 4 | 750
SBMS Summary Information
SBMS Summary Info #01 | 4 | 1001 | 4 | 1020
SBMS Summary Info #02 | 4 | 1021 | 4 | 1040
SBMS Summary Info #03 | 4 | 1041 | 4 | 1060
SBMS Summary Info #04 | 4 | 1061 | 4 | 1080
SBMS Summary Info #05 | 4 | 1081 | 4 | 1100
SBMS Summary Info #06 | 4 | 1101 | 4 | 1120
SBMS Summary Info #07 | 4 | 1121 | 4 | 1140
SBMS Summary Info #08 | 4 | 1141 | 4 | 1160
SBMS Summary Info #09 | 4 | 1161 | 4 | 1180
SBMS Summary Info #10 | 4 | 1181 | 4 | 1200
SBMS Summary Info #11 | 4 | 1201 | 4 | 1220
SBMS Summary Info #12 | 4 | 1221 | 4 | 1240
SBMS Summary Info #13 | 4 | 1241 | 4 | 1260
SBMS Summary Info #14 | 4 | 1261 | 4 | 1280
SBMS Summary Info #15 | 4 | 1281 | 4 | 1300
SBMS Summary Info #16 | 4 | 1301 | 4 | 1320
SBMS Summary Info #17 | 4 | 1321 | 4 | 1340
SBMS Summary Info #18 | 4 | 1341 | 4 | 1360
SBMS Summary Info #19 | 4 | 1361 | 4 | 1380
SBMS Summary Info #20 | 4 | 1381 | 4 | 1400
SBMS Detailed Information (Optionally Enabled) |  |  |  |  | These register are optionally enabled in the configuration setup
SBMS Detailed Information #01 | 4 | 10001 | 4 | 10100
SBMS Detailed Information #02 | 4 | 10101 | 4 | 10200
SBMS Detailed Information #03 | 4 | 10201 | 4 | 10300
SBMS Detailed Information #04 | 4 | 10301 | 4 | 10400
SBMS Detailed Information #05 | 4 | 10401 | 4 | 10500
SBMS Detailed Information #06 | 4 | 10501 | 4 | 10600
SBMS Detailed Information #07 | 4 | 10601 | 4 | 10700
SBMS Detailed Information #08 | 4 | 10701 | 4 | 10800
SBMS Detailed Information #09 | 4 | 10801 | 4 | 10900
SBMS Detailed Information #10 | 4 | 10901 | 4 | 11000
SBMS Detailed Information #11 | 4 | 11001 | 4 | 11100
SBMS Detailed Information #12 | 4 | 11101 | 4 | 11200
SBMS Detailed Information #13 | 4 | 11201 | 4 | 11300
SBMS Detailed Information #14 | 4 | 11301 | 4 | 11400
SBMS Detailed Information #15 | 4 | 11401 | 4 | 11500
SBMS Detailed Information #16 | 4 | 11501 | 4 | 11600
SBMS Detailed Information #17 | 4 | 11601 | 4 | 11700
SBMS Detailed Information #18 | 4 | 11701 | 4 | 11800
SBMS Detailed Information #19 | 4 | 11801 | 4 | 11900
SBMS Detailed Information #20 | 4 | 11901 | 4 | 12000